SECTION 08710 (08 78 03)

SPECIAL FUNCTION HARDWARE - DOOR SAFETY CONTROLS

Display hidden notes to specifier. (Don't know how? Click Here)

Copyright 2020 - 2024 ARCAT, Inc. - All rights reserved.

** NOTE TO SPECIFIER ** Miller Edge, Inc.; door hardware.

This section is based on the products of Miller Edge, Inc., which is located at:

300 N. Jennersville Rd.

P.O. Box 159
West Grove, PA 19390
Toll Free Tel:  800-220-3343
Tel:  610-869-4422
Fax:  610-869-4423
Email:  request info (info@milleredge.com)
Web:  http://www.milleredge.com

[Click Here] for additional information.

Miller Edge is the leading North American manufacturer of UL 325 recognized sensing solutions for motorized commercial and industrial doors and automated vehicular gate systems. The product line includes touch sensitive and non-contact devices such as sensing edges and photo eyes, in addition to a complete line of accessories designed to ease installati8on and enhance the level of safety for automatic door and gate systems.

GENERAL

SECTION INCLUDES

** NOTE TO SPECIFIER ** Delete doors and door sensors below not required for project.

Dorr installations must comply with certain safety standards, local codes, and UL325. The model numbers for sensors in parenthesis illustrate which sensors are suitable for each door type.

Entrapment Zone:  Leading Edge / Bottom of Door Sensors:

Sectional Doors:

Style:  Sensing Edge / Contact Device. (ME112) (ME113) (ME116) (ME117) (ME120) (ME123) (MU21) (MU22) (Clima-GUARD)

Style:  Photo Optics / Non-Contact Device. (MLC) (RLC) (OG-T) (TG-R)

Rolling Steel Doors:

Style:  Sensing Edge / Contact Device. (MC22)  (ME123) (MT21) (MT22)

Style:  Photo Optics / Non-Contact Device. (MLC) (RLC) (OG-T) (TG-R)

Bi-Fold Doors:

Style:  Sensing Edge / Contact Device. (ME123) (MU21) (MU22) (MU33) (MUxx)

Style:  Photo Optics / Non-Contact Device. (MLC) (RLC) (OG-T) (TG-R)

Countertop Grilles and Countertop Shutters:

Style:  Sensing Edge / Contact Device. (MC110) (ME110) (ME111) (ME112) (ME113) (ME120) (ME123)

Style:  Photo Optics / Non-Contact Device. (MLC) (RLC) (OG-T) (TG-R)

One-Piece Style Tilt Doors:

Style:  Sensing Edge / Contact Device. (ME120) (ME123)

Style:  Photo Optics / Non-Contact Device. (MLC) (RLC) (OG-T) (TG-R)

Rolling Shutter Doors:

Style:  Sensing Edge / Contact Device. (ME123) (MT21) (MT22)

Style:  Photo Optics / Non-Contact Device. (MLC) (RLC) (OG-T) (TG-R)

RELATED SECTIONS

** NOTE TO SPECIFIER ** Delete any sections below not relevant to this project; add others as required.

Section 08 33 00 - Coiling Doors and Grilles.

Section 08 33 13 - Coiling Counter Doors.

Section 08 34 00 - Special Function Doors.

Section 08 34 13 - Cold Storage Doors.

Section 08 35 00 - Folding Doors and Grilles.

Section 08 35 13.13 - Accordion Folding Doors.

REFERENCES

** NOTE TO SPECIFIER **  Entrapment zones for doors should be assessed per UL 325.

UL 325 is used as a basis to test products at a nationally recognized testing laboratory. Door operator manufacturers whose tested products are found to be in compliance with UL 325, they are “Listed” and receive a “Mark.” For information about gate system safety, visit DASMA (www.dasma.com) and Underwriter's Laboratories (www.ul.com).”

Underwriters Laboratories (UL):

UL 325 - Door, Drapery, Gate, Louver, and Window Operators and Systems.

SUBMITTALS

Submit under provisions of Section 01 30 00 - Administrative Requirements.

Product Data:

Manufacturer's data sheets on each product to be used.

Preparation instructions and recommendations.

Storage and handling requirements and recommendations.

Typical installation methods.

** NOTE TO SPECIFIER ** Delete if not applicable to product type.

Verification Samples:  Two representative units of each type, size, pattern, and color.

Shop Drawings:  Include details of materials, construction, and finish. Include relationship with adjacent construction.

QUALITY ASSURANCE

Manufacturer Qualifications:  Company specializing in manufacturing products specified in this section with a minimum of five years documented experience.

Installer Qualifications:  Company specializing in performing work of this section with minimum two years documented experience with projects of similar scope and complexity.

Source Limitations:  Provide each type of product from a single manufacturing source to ensure uniformity.

** NOTE TO SPECIFIER ** Include mock-up if the project size or quality warrant the expense. The following is one example of how a mock-up might be specified. When deciding on the extent of the mock-up, consider all the major different types of work on the project.

Mock-Up:  Construct a mock-up with actual materials in sufficient time for Architect's review and to not delay construction progress. Locate mock-up as acceptable to Architect and provide temporary foundations and support.

The intent of mock-up is to demonstrate quality of workmanship and visual appearance.

If mock-up is not acceptable, rebuild mock-up until satisfactory results are achieved.

Retain mock-up during construction as a standard for comparison with completed work.

Do not alter or remove mock-up until work is completed or removal is authorized.

PRE-INSTALLATION CONFERENCE

Convene a conference approximately two weeks before scheduled commencement of the Work. Attendees shall include Architect, Contractor and trades involved. Agenda shall include schedule, responsibilities, critical path items and approvals.

DELIVERY, STORAGE, AND HANDLING

Store and handle in strict compliance with manufacturer's written instructions and recommendations.

Protect from damage due to weather, excessive temperature, and construction operations.

PROJECT CONDITIONS

Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's recommended limits.

WARRANTY

Manufacturer's standard limited warranty unless indicated otherwise.

PRODUCTS

MANUFACTURERS

Acceptable Manufacturer:  Miller Edge, Inc., which is located at:  300 N. Jennersville Rd. P. O. Box 159; West Grove, PA 19390; Toll Free Tel:  800-220-3343; Tel:  610-869-4422; Fax:  610-869-4423; Email:  request info (tcastello@milleredge.com); Web:  http://www.milleredge.com.

** NOTE TO SPECIFIER ** Delete one of the following two paragraphs:  coordinate with requirements of Division 1 section on product options and substitutions.

Substitutions:  Not permitted.

Requests for substitutions will be considered in accordance with the provisions of Section 01 60 00 - Product Requirements.

SENSING EDGE / CONTACT DEVICES

** NOTE TO SPECIFIER ** Delete models and options not required. Model MC22 may be used on Rolling Steel doors.

Model MC22:  Pressure sensitive edge that is custom manufactured to specifications for length and outlet location. When touched lightly or at an angle, will send an immediate electrical signal to operator controls to stop, and/or reverse operations. Made with a vinyl wrapping and an extruded T. Designed to slide into applicable door’s bottom retainer.

ANSI/UL 325 Recognized Component.

End Flaps:  5 inch long. Creates a complete seal. Can be trimmed for custom fit.

Size (HxW):  2-1/4 x 3-1/4 inch (57 x 83 mm).

Length:  As specified, to nearest 0.25 inches (6 mm). Tolerance:  Plus or minus 1/4 inch (6 mm).

Edge Length for Sectional Doors:  Equal to the width of a sectional panel.

Edge Length for Rolling Steel Doors:  Equal to the distance between the tip of one guide to the tip of the opposite guide; ensures the active edge does not rub on the guides.

Maximum Length, Electric:  150 ft (45.72 m)

Maximum Length, Air-Wave:  60 ft (187.288 m).

Maximum Length, Pneumatic:  18 ft (5.486 m).

Lead Wire:  SJTO, 22 gauge, 2 ft (610 mm) length.

Sensitivity:  Nominal 3 to 6 lbf (1.8 to 3.2 kgf).

Electrical Maximum:  24 V AC/DC, 1/2 amp.

Electrical Configuration:  Normally open.

Exterior Materials:  Heavy duty reinforced PVC.

Contact Element:  Alumaglas.

Operating Temperature Range:  Meets or exceeds UL requirement.

Warranty:  1 year.

** NOTE TO SPECIFIER **  Delete wire outlet options not required.

Wire Outlet:  Universal

Wire Outlet:  Left

Wire Outlet:  Right.

** NOTE TO SPECIFIER **  Delete configuration options not required.

Monitored Configuration:  Sensing edges, photo optics, and accessories must meet the monitoring requirements of operator controls.

2-Wire. Electric.

10K resistor.

8.2K resistor.

Diode capacitor.

4-Wire. Electric.

Non-Monitored Configuration:

2-Wire. Electric. Edges contain two conductive strips.

Air-Wave. Non-monitored. Adjustable sensitivity. Flexible hose connected to an air switch.

Pneumatic. Non-monitored. Flexible hose, pneumatic switch.

** NOTE TO SPECIFIER **  Delete color/material options not required.

Color/Material:  Gray vinyl.

Color/Material:  Black vinyl.

Color/Material:  Yellow vinyl.

Color/Material:  Yellow and black striped vinyl.

Color/Material:  Yellow XR5 chemically resistant material.

** NOTE TO SPECIFIER **  The remaining items are optional. Delete options not required.

Coil Cord:  Attached.

Extra lead wire.

** NOTE TO SPECIFIER **  Model MC110 may be used on countertop grilles and countertop shutters.

Model MC110:  Designed for rolling counter shutter and grille applications, prioritizing both performance and aesthetics. When touched lightly or at an angle, MC110 sends an immediate signal to stop and/or reverse operation. This slide-in style sensing edge integrates a unique guide cap design that efficiently blocks light along the ends of the sensing edge. Additionally, the design contributes to enhancing building efficiency by minimizing air gaps. It further acts as a barrier to pests in food service areas. MC110 contributes to an integrated appearance that seamlessly complements the overall look of a counter shutter or grille.

ANSI/UL 325 Recognized Component.

Size (HxW):  3/4 x 7/8 inch (18 x 23 mm).

Length:  As specified, to nearest 0.25 inches (6 mm). Tolerance:  Plus or minus 1/4 inch (6 mm).

Edge Length for Sectional Doors:  Equal to the width of a sectional panel.

Edge Length for Rolling Steel Doors:  Equal to the distance between the tip of one guide to the tip of the opposite guide minus 2 inches (51 mm); ensures the active edge does not rub on the guides

Maximum Length, Electric:  50 ft (15.240 m).

Maximum Length, Air-Wave:  30 ft (9.144 m).

Lead Wire:  SJTO, 22 gauge, 2 ft (610 mm) length.

Sensitivity:  Nominal 4 to 7 lbf (1.8 to 3.2 kgf).

Electrical Maximum:  24 V AC/DC, 1/2 amp.

Electrical Configuration:  Normally open.

Exterior Materials:  Flexible PVC.

Contact Element:  Alumaglas.

Operating Temperature Range:  Meets or exceeds UL requirement.

Warranty:  1 year.

Mounting Channel:  ME110-C. Material:  Rigid PVC.

Kit Contents:

Edge Sensor:  ME110.

Mounting Channel:  ME110-C. Shape:  Flat. Material:  Rigid PVC.

Guide Caps:  Flexible PVC.

Color:  Black.

** NOTE TO SPECIFIER **  Delete wire outlet options not required.

Wire Outlet:  Left.

Wire Outlet:  Right.

Wire Outlet:  Top.

** NOTE TO SPECIFIER **  Delete configuration options not required.

Monitored Configuration:  Sensing edges, photo optics, and accessories must meet the monitoring requirements of operator controls.

2-Wire. Electric.

10K resistor.

8.2K resistor.

Diode capacitor.

4-Wire. Electric..

Non-Monitored Configuration:

2-Wire. Electric. Edges contain two conductive strips.

Air-Wave. Non-monitored. Adjustable sensitivity. Flexible hose connected to an air switch.

** NOTE TO SPECIFIER **  The Coil Cord is optional. Delete if not required.

Coil Cord:  Attached.

** NOTE TO SPECIFIER **  Model ME110 may be used on countertop grilles and countertop shutters.

Model ME110:  Pressure-sensitive edge adaptable to a variety of applications. When touched lightly or at an angle, sends a signal to stop and/or reverse operations. Multiple mounting channel designs allow installation on nearly any surface.

ANSI/UL 325 Recognized Component.

Size (HxW):  3/4 x 7/8 inch (18 x 23 mm).

Length:  As specified, to nearest 0.25 inches (6 mm). Tolerance:  Plus or minus 1/4 inch (6 mm).

Edge Length for Sectional Doors:  Equal to the width of a sectional panel.

Edge Length for Rolling Steel Doors:  Equal to the distance between the tip of one guide to the tip of the opposite guide minus 2 inches (51 mm); ensures the active edge does not rub on the guides.

Maximum Length, Electric:  50 ft (15.240 m).

Maximum Length, Air-Wave:  30 ft (9.144 m).

Lead Wire:  SJTO, 22 gauge, 2 ft (610 mm) length.

Sensitivity:  Nominal 4 to 7 lbf (1.8 to 3.2 kgf).

Electrical Maximum:  24 V AC/DC, 1/2 amp.

Electrical Configuration:  Normally open.

Exterior Materials:  Flexible PVC.

Contact Element:  Alumaglas.

Operating Temperature Range:  Meets or exceeds UL requirement.

Warranty:  1 year.

Color:  Black.

** NOTE TO SPECIFIER **  Delete wire outlet options not required.

Wire Outlet:  End.

Wire Outlet:  Left.

Wire Outlet:  Right.

Wire Outlet:  Top.

** NOTE TO SPECIFIER **  Delete configuration options not required.

Monitored Configuration:  Sensing edges, photo optics, and accessories must meet the monitoring requirements of operator controls.

2-Wire. Electric.

10K resistor.

8.2K resistor.

Diode capacitor.

4-Wire. Electric.

Non-Monitored Configuration.

2-Wire. Electric. Edges contain two conductive strips.

Air-Wave. Non-monitored. Adjustable sensitivity. Flexible hose connected to an air switch.

** NOTE TO SPECIFIER **  The Coil Cord is optional. Delete if not required.

Coil Cord:  Attached.

** NOTE TO SPECIFIER **  Delete mounting channel options not required.

Mounting Channel:  ME110-C. Material:  Rigid PVC.

Mounting Channel:  ME110-C2. Material:  Rigid PVC.

Mounting Channel:  ME110-C3. Material:  Rigid PVC.

** NOTE TO SPECIFIER **  Model ME111 may be used on countertop grilles and countertop doors.

Model ME111:  Pressure sensitive edge. Ideal for environments that have an uneven surface. When activated, sends a signal to stop and/or reverse operations. Mounting channel designs allow installation on nearly any surface.

ANSI/UL 325 Recognized Component.

Size (HxW):  1-1/2 x 7/8 inch (37 x 22 mm).

Length:  As specified, to nearest 0.25 inches (6 mm). Tolerance:  Plus or minus 1/4 inch (6 mm).

Edge Length for Sectional Doors:  Equal to the width of a sectional panel.

Edge Length for Rolling Steel Doors:  Equal to the distance between the tip of one guide to the tip of the opposite guide minus 2 inches (51 mm); ensures the active edge does not rub on the guides.

Maximum Length, Electric:  100 ft (30.480 mm).

Maximum Length, Air-Wave:  30 ft (9.144 m).

Lead Wire:  SJTO, 22 gauge, 2 ft (610 mm) length.

Sensitivity:  Nominal 4 to 7 lbf (1.8 to 3.2 kgf).

Electrical Maximum:  24 V AC/DC, 1/2 amp.

Electrical Configuration:  Normally open.

Exterior Materials:  Flexible PVC.

Contact Element:  Alumaglas.

Temperature Range:  Meets or exceeds UL requirement.

Warranty:  1 year.

Color:  Black.

** NOTE TO SPECIFIER **  Delete wire outlet options not required.

Wire Outlet:  End.

Wire Outlet:  Left.

Wire Outlet:  Right.

Wire Outlet:  Top.

** NOTE TO SPECIFIER **  Delete configuration options not required.

Monitored Configuration:  Sensing edges, photo optics, and accessories must meet the monitoring requirements of operator controls.

2-Wire. Electric.

10K resistor.

8.2K resistor.

Diode capacitor.

4-Wire. Electric.

Non-Monitored Configuration:

2-Wire. Electric. Edges contain two conductive strips.

Air-Wave. Non-monitored. Adjustable sensitivity. Flexible hose connected to an air switch.

** NOTE TO SPECIFIER **  The remaining items are optional. Delete options not required.

Coil Cord:  Attached.

Lead Wire:  10 ft.

** NOTE TO SPECIFIER **  Delete mounting channel options not required.

Mounting Channel:  ME110-C. Shape:  Flat. Material:  Rigid PVC.

Mounting Channel:  ME110-C2. Shape:  U. Material:  Rigid PVC.

Mounting Channel:  ME110-C3. Shape:  Flat with VHB tape. Material:  Rigid PVC.

** NOTE TO SPECIFIER **  Model ME112 may be used on sectional doors, countertop grilles, and countertop doors.

Model ME112:  Pressure sensitive edge that is custom manufactured to specifications for length and outlet location. When touched lightly or at an angle, will send an immediate electrical signal to operator controls to stop, and/or reverse operations. Retrofits to 1-3/8 inch (35 mm) sectional doors. The slide-in style edge has a double-T mounting design.

ANSI/UL 325 Recognized Component.

Size (HxW):  1-1/2 x 1-5/16 inch (38 x 34 mm).

Length:  As specified, to nearest 0.25 inches (6 mm). Tolerance:  Plus or minus 1/4 inch (6 mm).

Edge Length for Sectional Doors:  Equal to the width of a sectional panel.

Edge Length for Rolling Steel Doors:  Equal to the distance between the tip of one guide to the tip of the opposite guide minus 2 inches (51 mm); ensures the active edge does not rub on the guides.

Maximum Length, Electric:  100 ft (30.480 m).

Maximum Length, Air-Wave:  60 ft (187.288 m).

Maximum Length, Pneumatic:  18 ft (5.486 m).

Lead Wire:  SJTO, 22 gauge, 2 ft (610 mm) length.

Sensitivity:  Nominal 6 to 10 lbf (2.7 to 4.5 kgf).

Electrical Maximum:  24 V AC/DC,1/2 amp.

Electrical Configuration:  Normally open.

Exterior Materials:  Flexible PVC.

Contact Element:  Alumaglas.

Operating Temperature Range:  Meets or exceeds UL requirement.

Warranty:  1 year.

Color:  Black.

** NOTE TO SPECIFIER **  Delete configuration options not required.

Wire Outlet:  End.

Wire Outlet:  Left.

Wire Outlet:  Right.

Wire Outlet:  Top.

** NOTE TO SPECIFIER **  Delete configuration options not required.

Monitored Configuration:  Sensing edges, photo optics, and accessories must meet the monitoring requirements of operator controls.

2-Wire. Electric.

10K resistor.

8.2K resistor.

Diode capacitor.

4-Wire. Electric.

Non-Monitored Configuration:

2-Wire. Electric. Edges contain two conductive strips.

Air-Wave. Non-monitored. Adjustable sensitivity. Flexible hose connected to an air switch.

Pneumatic. Non-monitored. Flexible hose connected to an air switch.

** NOTE TO SPECIFIER **  The remaining items are optional. Delete options not required.

Coil Cord:  Attached.

Lead Wire:  10 ft.

** NOTE TO SPECIFIER **  Delete mounting option not required.

Mounting Channel:  ME112-C3. Shape:  L. Material:  Rigid PVC.

Mounting Channel:  ME112-C7. Shape:  Flat. Material:  Rigid PVC.

** NOTE TO SPECIFIER **  Model ME113 may be used on sectional doors, countertop grilles, and countertop doors.

Model ME113:  Pressure sensitive edge that is custom manufactured to specifications for length and outlet location. When touched lightly or at an angle, will send an immediate electrical signal to operator controls to stop, and/or reverse operations. Retrofits to 1-1/4 to 1-1/2 inch (32 to 38 mm) sectional doors. Slide-in style edge. Double-T mounting design.

ANSI/UL 325 Recognized Component.

Size (HxW):  1-9/16 x 1-1/2 inch (39 x 38 mm).

Length:  As specified, to nearest 0.25 inches (6 mm). Tolerance:  Plus or minus 1/4 inch (6 mm).

Edge Length for Sectional Doors:  Equal to the width of a sectional panel.

Edge Length for Rolling Steel Doors:  Equal to the distance between the tip of one guide to the tip of the opposite guide minus 2 inches (51 mm); ensures the active edge does not rub on the guides.

Maximum Length, Electric:  100 ft (30.480 m).

Maximum Length, Air-Wave:  60 ft (187.288 m).

Maximum Length, Pneumatic:  18 ft (5.486 m).

Lead Wire:  SJTO, 22 gauge, 2 ft (610 mm) length.

Sensitivity:  Nominal 7 to 12 lbf (3.2 to 5.4 kgf).

Electrical Maximum:  24 VAC/DC,1/2 amp.

Electrical Configuration:  Normally open.

Exterior Materials:  Flexible PVC.

Contact Element:  Alumaglas.

Operating Temperature Range:  Meets or exceeds UL requirement.

Warranty:  1 year.

Color:  Black.

** NOTE TO SPECIFIER **  Delete wire outlet options not required.

Wire Outlet:  Universal.

Wire Outlet:  End.

Wire Outlet:  Left.

Wire Outlet:  Right.

Wire Outlet:  Top.

** NOTE TO SPECIFIER **  Delete configuration options not required.

Monitored Configuration:  Sensing edges, photo optics, and accessories must meet the monitoring requirements of operator controls.

2-Wire. Electric.

10K resistor.

8.2K resistor.

Diode capacitor.

4-Wire. Electric.

Non-Monitored Configuration:

2-Wire. Electric. Edges contain two conductive strips.

Air-Wave. Non-monitored. Adjustable sensitivity. Flexible hose connected to an air switch.

Pneumatic. Non-monitored. Flexible hose, pneumatic switch.

** NOTE TO SPECIFIER **  The remaining items are optional. Delete options not required.

Coil Cord:  Attached.

Lead Wire:  10 ft.

End flaps.

Series connect option.

** NOTE TO SPECIFIER **  Delete mounting channel options not required.

Mounting Channels:  ME113-C. Shape:  U. Material:  Rigid PVC.

Mounting Channels:  ME113-C2. Shape:  U with shiplap. Material:  Rigid PVC.

Mounting Channels:  ME113-C3. Shape:  L. Material:  Rigid PVC.

Mounting Channels:  ME113-C7. Shape:  Flat. Material:  Rigid PVC.

** NOTE TO SPECIFIER **  Model ME116 may be used on sectional doors.

Model ME116:  Pressure sensitive edge that is specifically designed for 1-3/4 inch thick doors with a bottom retainer. When touched lightly or at an angle, will send an immediate electrical signal to operator controls to stop, and/or reverse operations. Slide-in style edge. Double-T mounting design. Fits CHI, Clopay, and Arm-R-Lite doors with double track bottom retainers. Will fit most doors 1-1/2 to 2 inches (38 to 51 mm) thick. Resistant to flame, water, and most common greases and oils.

ANSI/UL 325 Recognized Component.

Size (HxW):  1-1/2 x 1-13/16 inch (39 x 46 mm).

Length:  As specified, to nearest 0.25 inches (6 mm). Tolerance:  Plus or minus 1/4 inch (6 mm).

Edge Length for Sectional Doors:  Equal to the width of a sectional panel.

Edge Length for Rolling Steel Doors:  Equal to the distance between the tip of one guide to the tip of the opposite guide minus 2 inches (51 mm); ensures the active edge does not rub on the guides.

Maximum Length, Electric:  100 ft (30.480 m).

Maximum Length, Air-Wave:  60 ft (187.288 m).

Maximum Length, Pneumatic:  18 ft (5.486 m).

Lead Wire:  SJTO, 22 gauge, 2 ft (610 mm) length.

Sensitivity:  Nominal 7 to 12 lbf (3.2 to 5.4 kgf).

Electrical Maximum:  24 VAC/DC,1/2 amp.

Electrical Configuration:  Normally open.

Exterior Materials:  Flexible PVC.

Contact Element:  Alumaglas.

Operating Temperature Range:  Meets or exceeds UL requirement.

Warranty:  1 year.

Color:  Black.

Mounting:  Sensing edge slides into bottom section of door.

** NOTE TO SPECIFIER **  Delete configuration options not required.

Monitored Configuration:  Sensing edges, photo optics, and accessories must meet the monitoring requirements of operator controls.

2-Wire. Electric.

10K resistor.

8.2K resistor.

Diode capacitor.

4-Wire. Electric.

Non-Monitored Configuration:

2-Wire. Electric. Edges contain two conductive strips.

Air-Wave. Non-monitored. Adjustable sensitivity. Flexible hose connected to an air switch.

Pneumatic. Non-monitored. Flexible hose, pneumatic switch.

** NOTE TO SPECIFIER **  Delete outlet options not required.

Wire Outlet:  Universal end plug.

Wire Outlet:  End.

Wire Outlet:  Left.

Wire Outlet:  Right.

Wire Outlet:  Top.

** NOTE TO SPECIFIER **  The remaining items are optional. Delete options not required.

Coil Cord:  Attached.

Lead Wire:  10 ft.

End flaps.

** NOTE TO SPECIFIER **  Model ME117 may be used on sectional doors.

Model ME117:  Pressure sensitive electric edge with an added layer of PVC, creating a hollow pocket on the bottom of the edge. This hollow pocket conforms to irregularities in the surface which help prevent dust and debris from passing the threshold. When touch activated, electrically signals controls to stop and/or reverse operations. Will fit most doors from 1 to 2 inches (25 to 51 mm) thick.

ANSI/UL 325 Recognized Component.

Size (HxW):  2 x 1-7/8 inch (51 x 48 mm).

Length:  As specified, to nearest 0.25 inches (6 mm). Tolerance:  Plus or minus 1/4 inch (6 mm).

Edge Length for Sectional Doors:  Equal to the width of a sectional panel.

Edge Length for Rolling Steel Doors:  Equal to the distance between the tip of one guide to the tip of the opposite guide minus 2 inches (51 mm); ensures the active edge does not rub on the guides.

Maximum Length, Electric:  100 ft (30.480 m).

Maximum Length, Air-Wave:  60 ft (187.288 m).

Maximum Length, Pneumatic:  18 ft (5.486 m).

Length:  As specified, to nearest 0.25 inches (6 mm).

Lead Wire:  SJTO, 22 gauge, 2 ft (610 mm) length.

Sensitivity:  Nominal 8 to 13 lbf (3.6 to 5.9 kgf).

Wire Outlet:  Universal end plug.

Electrical Maximum:  24 VAC/DC,1/2 amp.

Electrical Configuration:  Normally open.

Exterior Materials:  Flexible PVC.

Contact Element:  Alumaglas.

Operating Temperature Range:  Meets or exceeds UL requirement.

Warranty:  1 year.

Color:  Black.

** NOTE TO SPECIFIER **  Delete configuration options not required.

Monitored Configuration:  Sensing edges, photo optics, and accessories must meet the monitoring requirements of operator controls.

2-Wire. Electric.

10K resistor.

8.2K resistor.

Diode capacitor.

4-Wire. Electric.

Non-Monitored Configuration:

2-Wire. Electric. Edges contain two conductive strips.

Air-Wave. Non-monitored. Adjustable sensitivity. Flexible hose connected to an air switch.

Pneumatic. Non-monitored. Flexible hose, pneumatic switch.

** NOTE TO SPECIFIER **  Delete outlet options not required.

Wire Outlet:  End.

Wire Outlet:  Left.

Wire Outlet:  Right.

Wire Outlet:  Top.

** NOTE TO SPECIFIER **  The remaining items are optional. Delete options not required.

Mounting Channel:  ME117-C7. Shape:  Flat. Material:  Rigid PVC.

Coil Cord:  Attached.

Lead Wire:  10 ft.

** NOTE TO SPECIFIER **  Model ME120 may be used on sectional doors, countertop grilles, countertop doors, and one-piece style tilt doors.

Model ME120:  Ideal for a variety of applications for motorized doors and gates and industrial safeguarding on manufacturing equipment. Applications Include:  Along conveyor systems detecting operator reach in, below lifts to protect from pinch points, and a variety of equipment where touch detection is desired.

UL 325 Recognized Component.

Size (HxW):  1-15/16 x 1-7/16 inch (49 x 36 mm).

Length:  As specified, to nearest 0.25 inches (6 mm). Tolerance:  Plus or minus 1/4 inch (6 mm).

Edge Length for Sectional Doors:  Equal to the width of a sectional panel.

Edge Length for Rolling Steel Doors:  Equal to the distance between the tip of one guide to the tip of the opposite guide minus 2 inches (51 mm); ensures the active edge does not rub on the guides.

Maximum Length, Electric:  100 ft (30.480 m).

Maximum Length, Air-Wave:  60 ft (187.288 m).

Maximum Length, Pneumatic:  18 ft (5.486 m).

Lead Wire:  SJTO, 22 gauge, 2 ft (610 mm) length.

Sensitivity:  Nominal 6 to 10 lbf (2.7 to 4.5 kgf).

Electrical Maximum:  24 VAC/DC,1/2 amp.

Electrical Configuration:  Normally open.

Exterior Materials:  Flexible PVC.

Contact Element:  Alumaglas.

Operating Temperature Range:  Meets or exceeds UL requirement.

Warranty:  1 year.

** NOTE TO SPECIFIER **  Delete configuration options not required.

Monitored Configuration:  Sensing edges, photo optics, and accessories must meet the monitoring requirements of operator controls.

2-Wire. Electric.

10K resistor.

8.2K resistor.

Diode capacitor.

4-Wire. Electric.

Non-Monitored Configuration:

2-Wire. Electric. Edges contain two conductive strips.

Air-Wave. Non-monitored. Adjustable sensitivity. Flexible hose connected to an air switch.

Pneumatic. Non-monitored. Flexible hose, pneumatic switch.

** NOTE TO SPECIFIER **  Delete color options not required.

Color:  Black.

Color:  Yellow.

** NOTE TO SPECIFIER **  Delete outlet options not required.

Wire Outlet:  End.

Wire Outlet:  Left.

Wire Outlet:  Right.

Wire Outlet:  Top.

** NOTE TO SPECIFIER **  The remaining items are optional. Delete options not required.

Coil Cord:  Attached.

Lead Wire:  10 ft.

Series connection option

** NOTE TO SPECIFIER **  Delete mounting channel options not required.

Mounting Channel:  ME120-C. Shape:  Flat. Material:  Aluminum.

Mounting Channel:  ME120-C5. Shape:  V. Material:  Aluminum.

Mounting Channel:  ME120-PC. Shape:  Flat. Material:  Rigid PVC.

** NOTE TO SPECIFIER **  Model ME123 may be used on sectional doors, rolling steel doors, bi-fold doors, countertop grilles, countertop doors, one-piece style tilt doors, and rolling shutter doors.

Model ME123:  Pressure sensitive edge that is custom manufactured to specifications for length and color. When touched lightly or at an angle, will send an immediate electrical signal to operator controls to stop, and/or reverse operations. Slide-in style edge. Double-T mounting design.

ANSI/UL 325 Recognized Component.

Size (HxW):  1-1/2 x 1-7/8 inch (38 x 48 mm).

Length:  As specified, to nearest 0.25 inches (6 mm). Tolerance:  Plus or minus 1/4 inch (6 mm).

Edge Length for Sectional Doors:  Equal to the width of a sectional panel.

Edge Length for Rolling Steel Doors:  Equal to the distance between the tip of one guide to the tip of the opposite guide minus 2 inches (51 mm); ensures the active edge does not rub on the guides.

Maximum Length, Electric:  100 ft (30.480 m).

Maximum Length, Air-Wave:  60 ft (187.288 m).

Maximum Length, Pneumatic:  18 ft (5.486 m).

Lead Wire:  SJTO, 22 gauge, 2 ft (610 mm) length.

Sensitivity:  Nominal 6 to 11 lbf (2.7 to 5 kgf).

Electrical Maximum:  24 V AC/DC,1/2 amp.

Electrical Configuration:  Normally open.

Exterior Materials:  Flexible PVC.

Contact Element:  Alumaglas.

Operating Temperature Range:  Meets or exceeds UL requirement.

Warranty:  1 year.

** NOTE TO SPECIFIER **  Delete configuration options not required.

Monitored Configuration:  Sensing edges, photo optics, and accessories must meet the monitoring requirements of operator controls.

2-Wire. Electric.

10K resistor.

8.2K resistor.

Diode capacitor.

4-Wire. Electric.

Non-Monitored Configuration:

2-Wire. Electric. Edges contain two conductive strips.

** NOTE TO SPECIFIER **  Delete color options not required.

Color:  Black.

Color:  Yellow.

** NOTE TO SPECIFIER **  Delete outlet options not required.

Wire Outlet:  Universal end plug.

Wire Outlet:  End.

Wire Outlet:  Left.

Wire Outlet:  Right.

Wire Outlet:  Top.

** NOTE TO SPECIFIER **  The remaining items are optional. Delete options not required.

Coil Cord:  Attached.

Lead Wire:  10 ft.

End flaps.

Series connect option.

** NOTE TO SPECIFIER **  Delete mounting channel options not required.

Mounting Channel:  ME123-C. Shape:  U. Material:  Rigid PVC.

Mounting Channel:  ME123-C1. Shape:  T. Material:  Rigid PVC.

Mounting Channel:  ME123-C2175. Shape:  U with shiplap. Material:  Rigid PVC.

Mounting Channel:  ME123-C3. Shape:  L. Material:  Rigid PVC.

Mounting Channel:  ME123-CA3. Shape:  L. Material:  Aluminum.

Mounting Channel:  ME123-C7. Shape:  Flat. Material:  Rigid PVC.

Model Series:  MT. Pressure sensitive edge covered in a durable vinyl jacket. Custom manufactured specifications for length, width, height, and sensitivity. When touched lightly sends signal to controls to stop, and/or reverse operations. Contours to curved surfaces. Acts as a weatherstrip on doors. The top tab inserts between the double-L angle bottoms bars on a rolling door. These sensing edges are flexible and can conform to irregularities in the floor.

ANSI/UL 325 Recognized Component.

End Flaps:  5 inch long. Creates a complete seal. Can be trimmed for custom fit.

** NOTE TO SPECIFIER **  Delete model options not required. Models MT21, MT22, and MT33 may be used on rolling steel doors and rolling shutter doors.

Model MT21. Size (HxW):  1 x 2 inches (25 x 51 mm).

Model MT22. Size (HxW):  2 x 2 inches (51 x 51 mm).

Model MT33. Size (HxW):  3 x 3 inches (76 x 76 mm).

Length:  As specified, to nearest 0.25 inches (6 mm). Tolerance:  Plus or minus 1/4 inch (6 mm).

Edge Length for Sectional Doors:  Equal to the width of a sectional panel.

Edge Length for Rolling Steel Doors:  Equal to the distance between the tip of one guide to the tip of the opposite guide minus 2 inches (51 mm); ensures the active edge does not rub on the guides.

Maximum Length, Electric:  150 ft (45.72 m).

Maximum Length, Air-Wave:  60 ft (187.288 m).

Maximum Length, Pneumatic:  18 ft (5.486 m).

Lead Wire:  SJTO, 22 gauge, 2 ft (610 mm) length.

Sensitivity:  Nominal 4 to 8 lbf (1.8 to 3.6 kgf).

Electrical Maximum:  24 V AC/DC, 1/2 amp.

Electrical Configuration:  Normally open.

Exterior Materials:  Heavy duty reinforced PVC.

Contact Element:  Alumaglas.

Operating Temperature Range:  Meets or exceeds UL requirement.

Warranty:  1 year.

Mounting:  Between bottom bars. Horizontal mount.

** NOTE TO SPECIFIER **  Delete configuration options not required.

Monitored Configuration:  Sensing edges, photo optics, and accessories must meet the monitoring requirements of operator controls.

2-Wire. Electric.

10K resistor.

8.2K resistor.

Diode capacitor.

4-Wire. Electric.

Non-Monitored Configuration:

2-Wire. Electric. Edges contain two conductive strips.

Air-Wave. Non-monitored. Adjustable sensitivity. Flexible hose connected to an air switch.

Pneumatic. Non-monitored. Flexible hose, pneumatic switch.

** NOTE TO SPECIFIER **  Delete outlet options not required.

Wire Outlet:  Universal.

Wire Outlet:  Left.

Wire Outlet:  Right.

** NOTE TO SPECIFIER **  Delete color/material options not required.

Color/Materials:  Gray vinyl.

Color/Materials:  Black vinyl.

Color/Materials:  Yellow vinyl.

Color/Materials:  Yellow and black striped vinyl.

Color/Materials:  Yellow XR5 chemically resistant material.

** NOTE TO SPECIFIER **  The remaining items are optional. Delete options not required.

Series connection option.

Coil Cord:  Attached.

Lead Wire:  10 ft.

Vinyl loop.

Model Series MU. Direct mount. Pressure sensitive electric edge When touched lightly or at an angle, sends signal to controls to stop and/or reverse operations. Flexible and contours curved surfaces. Covered in durable vinyl jacket. Conforms to floor irregularities. The top tabs wrap around the leading edge of a sectional door.

ANSI/UL 325 Recognized Component.

End Flaps:  5 inch long. Creates a complete seal. Can be trimmed for custom fit.

** NOTE TO SPECIFIER **  Delete model options not required.

Model MU21, MU22, and MU33 may be used on sectional doors and bi-fold doors.

Model MU21. Size (HxW):  1 x 2 inches (25 x 51 mm).

Model MU22. Size (HxW):  2 x 2 inches (51 x 51 mm).

Model MU33. Size (HxW):  3 x 3 inches (76 x 76 mm).

Length:  As specified, to nearest 0.25 inches (6 mm). Tolerance:  Plus or minus 1/4 inch (6 mm).

Edge Length for Sectional Doors:  Equal to the width of a sectional panel.

Edge Length for Rolling Steel Doors:  Equal to the distance between the tip of one guide to the tip of the opposite guide minus 2 inches (51 mm); ensures the active edge does not rub on the guides.

Maximum Length, Electric:  150 ft (45.72 m).

Maximum Length, Air-Wave:  60 ft (187.288 m).

Maximum Length, Pneumatic:  18 ft (5.486 m).

Lead Wire:  SJTO, 22 gauge, 2 ft (610 mm) length.

Sensitivity:  Nominal 4 to 8 lbf (1.8 to 3.6 kgf).

Electrical Maximum:  24 V AC/DC, 1/2 amp.

Electrical Configuration:  Normally open.

Exterior Materials:  Heavy duty reinforced PVC.

Contact Element:  Alumaglas.

Operating Temperature Range:  Meets or exceeds UL requirement.

Warranty:  1 year.

Mounting:  Tabs.

** NOTE TO SPECIFIER **  Delete configuration options not required.

Monitored Configuration:  Sensing edges, photo optics, and accessories must meet the monitoring requirements of operator controls.

2-Wire. Electric.

10K resistor.

8.2K resistor.

Diode capacitor.

4-Wire. Electric.

Non-Monitored Configuration:

2-Wire. Electric. Edges contain two conductive strips.

Air-Wave. Non-monitored. Adjustable sensitivity. Flexible hose connected to an air switch.

Pneumatic. Non-monitored. Flexible hose, pneumatic switch.

** NOTE TO SPECIFIER **  Delete wire outlet options not required.

Wire Outlet:  Universal.

Wire Outlet:  Left.

Wire Outlet:  Right.

** NOTE TO SPECIFIER **  Delete color/materials options not required.

Color/Materials:  Gray vinyl.

Color/Materials:  Black vinyl.

Color/Materials:  Yellow vinyl.

Color/Materials:  Yellow and black striped vinyl.

Color/Materials:  Yellow XR5 chemically resistant material.

** NOTE TO SPECIFIER **  The remaining items are optional. Delete options not required.

Series connection option.

Coil Cord:  Attached.

Lead Wire:  10 ft.

** NOTE TO SPECIFIER **  Model MUxx may be used on bi-fold doors.

Model:  MUxx. Completely customizable for profile height and width, active edge length, and outlet location, and sensitivity. When touched sends a signal to controls to stop, and/or reverse operations. Contours to curved surfaces. Covered in a durable vinyl jacket. The top mounting tabs wrap around the leading edge of a sectional or hangar door.

ANSI/UL 325 Recognized Component.

End Flaps:  6 inch long. Creates a complete seal. Can be trimmed for custom fit.

Size (HxW):  Custom. Profile:  Square, rectangular, or angled.

Length:  As specified, in 1 inch (25 mm) increments. Tolerance:  Plus or minus 1/4 inch (6 mm).

Edge Length for Sectional Doors:  Equal to the width of a sectional panel.

Edge Length for Rolling Steel Doors:  Equal to the distance between the tip of one guide to the tip of the opposite guide minus 2 inches (51 mm); ensures the active edge does not rub on the guides.

Maximum Length, Electric:  150 ft (45.72 m).

Maximum Length, Air-Wave:  60 ft (187.288 m).

Maximum Length, Pneumatic:  18 ft (5.486 m).

Lead Wire:  SJTO, 22 gauge, 2 ft (610 mm) length.

Sensitivity:  Based on custom dimensions.

Electrical Maximum:  24 V AC/DC, 1/2 amp.

Electrical Configuration:  Normally open.

Exterior Materials:  Heavy duty reinforced PVC.

Contact Element:  Alumaglas.

Operating Temperature Range:  Meets or exceeds UL requirement.

Warranty:  1 year.

Mounting:  Tabs.

** NOTE TO SPECIFIER **  Delete configuration options not required.

Monitored Configuration:  Sensing edges, photo optics, and accessories must meet the monitoring requirements of operator controls.

2-Wire. Electric.

10K resistor.

8.2K resistor.

Diode capacitor.

4-Wire. Electric.

Non-Monitored Configuration:

2-Wire. Electric. Edges contain two conductive strips.

Air-Wave. Non-monitored. Adjustable sensitivity. Flexible hose connected to an air switch.

Pneumatic. Non-monitored. Flexible hose, pneumatic switch.

** NOTE TO SPECIFIER **  Delete wire outlet options not required.

Wire Outlet:  Universal.

Wire Outlet:  Left.

Wire Outlet:  Right.

** NOTE TO SPECIFIER **  Delete color/material options not required.

Color/Material:  Gray vinyl.

Color/Material:  Black vinyl.

Color/Material:  Yellow vinyl.

Color/Material:  Yellow and black striped vinyl.

Color/Material:  Yellow XR5 chemically resistant material.

** NOTE TO SPECIFIER **  The remaining items are optional. Delete options not required.

Series connection with optional quick micro connectors.

Coil Cord:  Attached.

Extra lead wire.

Vinyl loop.

** NOTE TO SPECIFIER **  Clima-GUARD may be used on sectional doors.

Clima-GUARD:  Direct mount. Pressure-sensitive electric edge with an added layer of protection. Provides a weather seal for doors having uneven thresholds, eliminating risk of damaging edge from over-compression. Touch activated, sending signal to stop and/or reverse. Retrofits easily to 2 inch (51 mm) sectional doors.

ANSI/UL 325 Recognized Component.

Size (HxW):  3 x 2-1/4 inches (76 x 57 mm).

Length:  As specified, to nearest 0.25 inches (6 mm). Tolerance:  Plus or minus 1/4 inch (6 mm).

Edge Length for Sectional Doors:  Equal to the width of a sectional panel.

Edge Length for Rolling Steel Doors:  Equal to the distance between the tip of one guide to the tip of the opposite guide minus 2 inches (51 mm); ensures the active edge does not rub on the guides.

Maximum Length, Electric:  100 ft (30.480 m).

Maximum Length, Air-Wave:  60 ft (187.288 m).

Lead Wire:  SJTO, 22 gauge, 2 ft (610 mm) length.

Sensitivity:  Nominal 6 to 10 lbf (2.7 to 4.5 kgf).

Electrical Maximum:  24 V AC/DC,1/2 amp.

Electrical Configuration:  Normally open.

Exterior Materials:  Flexible PVC.

Contact Element:  Alumaglas.

Operating Temperature Range:  Meets or exceeds UL requirement.

Warranty:  1 year.

Color:  Black.

** NOTE TO SPECIFIER **  Delete configuration options not required.

Monitored Configuration:  Sensing edges, photo optics, and accessories must meet the monitoring requirements of operator controls.

2-Wire. Electric.

10K resistor.

8.2K resistor.

Diode capacitor.

4-Wire. Electric.

Non-Monitored Configuration:

2-Wire. Electric.

Air-Wave. Non-monitored. Adjustable sensitivity. Flexible hose connected to an air switch.

** NOTE TO SPECIFIER **  Delete outlet options not required.

Wire Outlet:  End.

Wire Outlet:  Left..

Wire Outlet:  Right

Wire Outlet:  Top.

** NOTE TO SPECIFIER **  The remaining items are optional. Delete options not required.

Coil Cord:  Attached.

Extra lead wire.

Series connect option.

** NOTE TO SPECIFIER **  Delete mounting channel options not required.

Mounting Channel:  ME112-C4. Shape:  U. Material:  Rigid PVC.

Mounting Channel:  ME112-C43. Shape:  L. Material:  Rigid PVC.

Mounting Channel:  ME112-C47. Shape:  Flat. Material:  Rigid PVC.

** NOTE TO SPECIFIER **  Delete article not required. the models in this article may be used sectional doors, rolling steel doors, bi-fold doors, countertop grilles, countertop doors, one-piece style tilt doors, and rolling shutter doors.

PHOTO OPTICS / NON-CONTACT DEVICES

Model MLC:  Monitored Light Curtain. A series of thru-beam photo eyes providing a dense barrier of protection while being monitored for presence and function by the door operator. When interrupted, the door operator is signaled to reverse operation. Ideal for sensing protruding parts that may not be detected by a standard single-beam photo eye mounted 6 inches from the floor.

UL 325 Recognized Component. IP67 waterproof housing.

IP67 waterproof housing.

Span (WxH):  Up to 32 x 6 ft (10 x 1.8 m).

Operating Range:  8 to 32 ft (2 to 10 m).

** NOTE TO SPECIFIER **  Delete model option not required.

Model No. MLC-K36:  3 ft (1 m). Number of Elements:  8. Monitored.

Dimensions (WxHxD):  1 x 38 x 1.1 inches (25 x 1000 x 28 mm).

Mounting:  Four, universal mounting brackets.

Model No. MLC-K72:  6 ft (2 m). Number of Elements:  16. Monitored.

Dimensions (WxHxD):  1 x 74 x 1.1 inches (25 x 2000 x 28 mm).

Mounting:  Six, universal mounting brackets.

Housing Material:  PVC over aluminum.

LED Indicators EM:  Power, Obstruction RX:  Power EM:  Power, Obstruction RX:  Power.

Cable Length EM:  36 in. (1 m) RX:  36 in. (1 m) EM:  36 in. (1 m) RX:  36 in. (1 m)

Ambient Light:  Greater than 100,000 lux.

Aperture Angle EM:  Plus or minus 8 degrees. RX:  Plus or minus 15 degrees.

Electrical:

Supply Voltage:  12-24 V AC/DC.

Current Consumption:  Less than 100 mA at 24 volts DC.

Output:  4-wire pulse (2-power, 2-pulsed).

Frequency:  325 Hz.

Temperature Range:  -40 to 140 degrees F (-40 to 60 degrees C).

Indoor and outdoor use.

Model RLC :  Relay  Light Curtain. A fail-safe multiple thru-beam photo optic providing a dense barrier of protection. When interrupted, the door is signaled to stop and/or reverse. For environments requiring vertical protection for protruding parts not detected by a standard single-beam photo eye.

UL 325 Recognized Component. IP67 waterproof housing.

IP67 waterproof housing.

Span (WxH):  Up to 32 x 6 ft (10 x 1.8 m).

Operating Range:  8 to 32 ft (2 to 10 m).

Thru-beam technology minimizes false reflective signals.

Model No:  ·RLC-K36:  3 ft (1 m). Number of Elements:  8.

Dimensions (WxHxD):  1 x 38 x 1.1 inches (25 x 1000 x 28 mm).

Mounting:  Four, universal mounting brackets.

Model No:  RLC-K72:  6 ft (2 m). Number of Elements:  16.

Dimensions (WxHxD):  1 x 74 x 1.1 inches (25 x 2000 x 28 mm).

Mounting:  Six, universal mounting brackets.

Housing Material:  PVC over aluminum.

LED Indicators EM:  Power, Obstruction RX:  Power EM:  Power, Obstruction RX:  Power.

Cable Length EM:  50 ft. (15 m) RX:  50 ft (15 m).

Ambient Light:  Greater than 100,000 lux.

Aperture Angle EM:  Plus or minus 8 degrees. RX:  Plus or minus 15 degrees.

Electrical:

Supply Voltage:  12-24 V AC/DC.

Current Consumption:  Less than 150 mA at 24 volts DC.

Output:  N.O. and N.C.

Frequency:  325 Hz.

Temperature Range:  -40 to 140 degrees F (-40 to 60 degrees C).

Indoor and outdoor use.

Non-Monitored, Fail-Safe Device.

Simplified Wiring:  No external interface box.

LED Indicators EM:  Power, Obstruction RX:  Power EM:  Power, Obstruction RX:  Power

Warranty:  2 years.

Model OG-T:  OptiGuard. Monitored Thru-Beam Photo Eye. Thru-beam entrapment protection for door and gate operators. When an obstruction interrupts the beam, a signal is sent to motor controls to stop and/or reverse motion. Mounting bracket/hoods offer protection against debris, weather and the sun. Easy alignment using a visible beam of light.

UL 325 Recognized Component. IP67 waterproof housing.

IP67 waterproof housing.

Operating Range:  6 to 100 ft (2 to 30 m).

Number of Elements:  1.

Maximum Ambient Light:  Greater than 100,000 lux.

Aperture Angle:  Plus or minus 3 degrees.

Operating Temperature:  -13 to 131 degrees F (-25 to 55 degrees C).

Power Source:  12 to 40 volts DC, 24 to 48 volts AC.

Current Consumption:  Less than 40 mA.

Relay Rating:  2 Amps at 40 volts AC/DC.

Output:  Normally closed. 10K.

Warranty:  2 years.

Emitter:

Dimensions (WxHxD):  0.75 x 2.5 x 1.38 inches. (19 x 64 x 35 mm).

Weight:  5.5 oz.

Housing Material:  Polycarbonate, PMMA lens.

LED Indicators:  1:  Power.

Cable Length:  6 ft., 20 AWG cable; attached.

Mounting Orientation:  Horizontal or vertical.

Degree of Protection:  IP67.

Receiver:

Dimensions (WxHxD):  0.75 x 2.5 x 1.38 inches. (19 x 64 x 35 mm).

Weight:  5.5 oz.

Housing Material:  Polycarbonate, PMMA lens.

LED Indicators:  2:  Power, alignment.

Cable Length:  6 ft., 20 AWG cable; attached.

Mounting Orientation:  Horizontal or vertical.

Degree of Protection IP67.

Mounting Bracket / Hoods:

Dimensions (WxHxD):  1.75 x 4 x 2.38 inches (44 x 102 x 60 mm).

Weight:  5.5 oz.

Housing Material:  Galvanized.

Mounting Orientation:  Horizontal or vertical.

** NOTE TO SPECIFIER **  Delete model option not required.

OG-T-K10:  OptiGuard:  Normally Closed,10K, 100 ft. range.

OG-T-PKIT:  OptiGuard:  Pulsed, 100 ft. range. Includes one operator interface module, Model SM-102.

** NOTE TO SPECIFIER **  The remaining item is optional. Delete option if not required.

PE-CON-K10:  Photo Eye Conduit Enclosure Kit with conduit body for 3/4 inch conduit.

Model TG-R:  TruGuard. Monitored Reflective Photo Eye. Combines the emitter and receiver in one housing. The hooded reflector returns the photo optic beam to the emitter/receiver unit. When an obstruction interrupts the beam, a signal is sent to motor controls to stop and/or reverse motion. Easy alignment using a visible beam of light.

UL 325 Recognized Component. IP67 waterproof housing.

IP67 waterproof housing.

Operating Range:  6 to 30 ft (2 to 9 m).

Number of Elements:  1.

Maximum Ambient Light:  Greater than 100,000 lux.

Aperture Angle:  Plus or minus 3 degrees.

Reflector:  Corner cube.

Operating Temperature:  -13 to 131 degrees F (-25 to 55 degrees C).

Power Source:  12 to 40 volts DC, 24 to 48 volts AC.

Current Consumption:  Less than 40 mA.

Relay Rating:  2 Amps at 40 volts AC/DC.

Output:  Normally closed. 10K pulsed.

Warranty:  2 years.

Emitter/Receiver:

Dimensions (WxHxD):  0.75 x 2.5 x 1.38 inches. (19 x 64 x 35 mm).

Weight:  5.5 oz.

Housing Material:  EM/RX:  Polycarbonate, PMMA lens.

LED Indicators:  2:  Power and alignment.

Cable Length:  6 ft., 20 AWG cable; attached.

Mounting Orientation:  Horizontal or vertical.

Degree of Protection:  IP67.

Mounting Bracket:

Dimensions (WxHxD):  1.75 x 4 x 2.38 inches. (44 x 102 x 60 mm).

Weight:  6.5 oz.

Housing Material:  Galvanized steel.

LED Indicators:  2:  Power and alignment.

Cable Length:  6 ft., 20 AWG cable; attached.

Mounting Orientation:  Horizontal or vertical.

Degree of Protection:  IP67.

Reflector/Hood:

Dimensions (WxHxD):  3.94 x 3.94 x 1.86 inches (100 x 100 x 47 mm).

Weight:  6.5 oz.

Housing Material:  Reflector:  PMMA/ABS. Hood:  Plastic.

Mounting Orientation:  Vertical.

** NOTE TO SPECIFIER **  Delete model option not required.

TG-R-K10:  TruGuard:  Normally Closed,10K, 30 ft. range.

TG-R-PKIT:  TruGuard:  Pulsed. 30 ft. range. Includes one operator interface module, Model SM-102.

** NOTE TO SPECIFIER **  The remaining item is optional. Delete option not required.

PE-CON-K10:  Photo Eye Conduit Enclosure Kit with conduit body for 3/4 inch conduit.

** NOTE TO SPECIFIER ** Delete article if not required. Because Motion Sensors do not qualify as entrapment devices, they are not required by UL 325.

MOTION SENSORS

Model:  MWave. Intelligent radar motion detector for doors. Fully customizable, hands-free equipped with dual relays. Provides detection capabilities that differentiate between approaching versus cross-traffic, and pedestrian versus vehicular traffic. Preconfigured for a wide range of applications. Optional remote control.

Technology:  Doppler radar. Indoor and outdoor.

Detection Mode:  Radar motion sensor.

Minimum Detection Speed:  2 inches (51 mm) per second minimum.

Response Time:  Less than 100 milliseconds.

Output Hold Time:  0.5 to 300 seconds; adjustable.

Operating Temperature Range:  -22 to 140 degrees F (-30 degrees to 60 degrees C).

Humidity:  Maximum 90 percent non-condensing.

Switching Voltage:  48 V AC/DC, 1/2 amp.

Power Source:  12 to 36 volts DC, 12 to 28 volts AC.

Output:  2 channel. Normally open or normally closed; selectable.

Max Power Consumption:  Less than 1 W.

Enclosure Material:  Polycarbonate.

Color:  Black.

LED Indicators:  2 red/green bi-color.

LEDs:  Power, programing, and detection.

Warranty:  3 years.

Mounting Height:  Minimum:  10 ft. (3 m). Maximum:  23 ft. (7 m).

Dimensions (WxHxD):

With mounting bracket (180 degree):  5-1/8  x 2-7/8 x 5-3/8 inches (131 x 73 x 136 mm).

Without mounting bracket:  5-1/8 x 2-7/8 x 3-7/8 inches. (131 x 73 x 98 mm).

Weight 11.5 oz. With Cable:  23 oz.

Detection Zone (WxD):

Installation Height of 16 ft (5 m) and Inclination Angle of 45 degrees:  21 x 29 ft. (9 x 6.5 m).

Installation Height of 23 ft. (7 m) and Inclination Angle of 45 degrees:  18 x 32 ft. (10 x 5.5 m).

Degree of Protection:  IP67, NEMA 6.

Mounting Angle:  Plus or minus 90 degrees in 15 degree increments.

ACCESSORIES

** NOTE TO SPECIFIER ** Delete accessories and options not required.

Wireless sensing edge transmitters and receivers.

Model:  RB-P-K10C. RB and Monitored Wireless Door Transmitter and Receiver. For automated door systems.

Eliminates need to hardwire Sensing Edges to the operator.

Bi-directional communication between the Transmitter and the Receiver improve immunity to RF interference.

Onboard diagnostics.

Single-Channel Non-Monitored Wireless System Sensing Edge System. Provides wireless signal transmission from the sensing edge to motor controls. On-board diagnostics. Transmitter:  comes in NEMA 4 weather-proof enclosure. Transparent cases.

Response Time:  30 milliseconds.

Operating Temperature:  0 to 130 degrees F (-18 to 55 degrees C).

Frequency:  318 MHz.

Operating Range:  100 ft. (optimal conditions).

Warranty:  2 years.

Receiver:

Power Source:  12 to 24 volts AC/DC nominal.

Nominal:  60 mA.

Activated:  140 mA activated.

Input/Output:  Output:  Normally open, normally closed.

Dimensions (WxHxD):  3-3/4 x 4-13/16 x 1-1/4 inches (95 x 122 x 32 mm).

Weight:  4.6 oz.

Enclosure Material:  Polycarbonate.

LED Indicators:  Power, status, channel 1.

Antenna:  Attached wire or F connector.

Transmitter:

Two, 1.5 volts AA alkaline batteries,  2-year expectancy.

Input/Output:  Input:  2-wire N.O. sensing edge.

Dimensions (WxHxD):  1-13/16 x 5-3/4 x 1-3/4 inches (46 x 146 x 44 mm).

Weight:  7.2 oz.

Enclosure Material:  Polycarbonate.

LED Indicators:  Transmit.

Degree of Protection:  NEMA 4.

Alarm:  80-95 dB at 2ft (MWRTA12B only).

** NOTE TO SPECIFIER **  Delete model option not required.

Model:  MWRT12B.

Model:  MWRTA12B. With low battery audible alarm. Activates when battery has 25 percent remaining life.

Model:  AW14-RF-K10 – Wireless Air-Wave non-monitored wireless sensing edge system. utilizes air pressure, via an Air-Wave sensing edge, to activate a diaphragm contact within the wireless transmitter switch. This contact converts the pressure wave into an electrical contact, which alerts the operator to stop and/or reverse when there is an obstruction. Eliminates the need to hardwire coil cords and retracting reels.

Operating Temperature:  14 to 158 degrees F (-10 to 70 degrees C).

Frequency:  915 MHz.

Operating Range:  50 ft (15 m) nominal; 100 ft. (30 m) maximum optimal conditions.

Maximum Pneumatic Load:  78.70 inches (2,000 mm) water column.

Adjustable Sensitivity:  0.078 to 19.70 inches (2 to 500 mm) water column.

Receiver:

Power Source:  10 to 40 volts AC, 10 to 30 volts DC battery.

Input/Output:  Output:  2-wire, Normally open.

Dimensions (WxHxD):  3-3/4 x 4-7/16 x 1-1/4 inches. (95 x 113 x 32 mm).

Weight:  3.9 oz.

Enclosure Materials:  Polycarbonate.

LED Indicators:  Power, status, channel 1.

Antenna:  Attached wire.

Transmitter:

Power Source:  One, CR2032 3 volt lithium battery.

Input/Output:  Input:  Miller Edge Air-Wave sensing edge.

Dimensions (WxHxD):  1-15/16 x 3-3/8 x 1-11/16 inches. (50 x 85 x 43 mm).

Weight:  4.5 oz.

Enclosure Materials:  ABS enclosure, silicone diaphragm, silicone tubing, barbed coupler.

LED Indicators:  Transmit.

Antenna:  Attached wire.

Operator interface modules:

Signature Module:  Emulates a monitored pulsed signal required by some commercial door operators.

** NOTE TO SPECIFIER **  Delete model option not required.

Model:  SM-101 – Converts a diode capacitor signal to pulsed.

UL 325 Recognized Component.

Operating Temperature:  -31 to 158 degrees F (-35 to 70 degrees C).

Power Source:  Photo eye input.

Current Consumption:  30 mA.

Input:  Diode capacitor (monitored) sensing edge.

Output:  Pulsed (monitored).

Relay Rating:  Class 2 device.

Dimensions:

Module (HxWxD):  1.8 x 1.25 x 0.8 inches (46 x 32 x 20 mm).

Junction Box (HxWxD):  1.5 x 4 x 2 inches (38 x 102 x 51 mm).

Weight:  12 oz.

Housing Material:

Module:  ABS plastic with epoxy.

Junction Box:  Galvanized steel.

LED Indicators:  Power, fault.

Degree of Protection:

Module:  NEMA 4.

Junction Box:  UL Listed.

Model:  SM-102 –  Converts a 10K resistive signal to pulsed.

UL 325 Recognized Component.

Operating Temperature:  -31 to 158 degrees F (-35 to 70 degrees C).

Power Source:  Photo eye input.

Current Consumption:  30 mA.

Input:  10K resistive (monitored) sensing edge.

Output:  Pulsed (monitored).

Relay Rating:  Class 2 device.

Dimensions:

Module (HxWxD):  1.8 x 1.25 x 0.8 inches (46 x 32 x 20 mm).

Junction Box (HxWxD):  1.5 x 4 x 2 inches (38 x 102 x 51 mm).

Weight:  12 oz.

Housing Material:

Module:  ABS plastic with epoxy.

Junction Box:  Galvanized steel.

LED Indicators:  Power, fault.

Degree of Protection:

Module:  NEMA 4.

Junction Box:  UL Listed.

Air-Wave Edge Switches:  Sensing Edge Accessory. For wet and/or refrigerated areas subject to condensation, cold climates, high vibration environments, and where a monitored electric sensing edge is not ideal. The switch activates when a wave of air is compressed through an air hose and triggers the internal diaphragm converting a pressure wave into an electrical contact, which signals the commercial door operator to stop and/or reverse motion. Switches sensitivity is adjustable. Compatible with Air-Wave configured sensing edges and treadles. Non-monitored.

Detection Technology:  Air pressure.

Maximum Pressure:  3 psi.

Maximum Switch Frequency:  25 per second.

Adjustable Sensitivity 0.078 to 19.7 inches (2 to 500 mm) water column.

Maximum Edge Length:  60 ft.

Operating Temperature Range:  -49 to 180 degrees F (-45 to 82 degrees C) Mechanical Life:  Minimum 1,000,000 operations.

Output:  Normally open or normally closed.

Maximum Contact Load:  0.5 amps, 220 volts AC; 1 A, 48 volts DC.

Electrical Configuration:  2-wire, Normally open.

Terminal Configuration 0.187 in. Q.C. tabs.

Components:

Junction Boxes.

Coil Cords.

End Plugs.

Gum Rubber Air Hose.

Retracting Reels.

** NOTE TO SPECIFIER **  Delete model option not required.

Model:  AW10 – Air-Wave switch.

Dimensions (WxHxD):  1-3/4 x 1-1/4 x 1-1/4 inches (44 x 32 x 32 mm).

Weight:  0.5 oz.

Housing Material:  ABS.

Mounting:  Screw tabs.

Model:  AW12 – AW10 switch in NEMA 4 polycarbonate enclosure.

Dimensions (WxHxD):  1-13/16 x 6-3/4 x 1-3/4 inches (44 x 32 x 32 mm).

Weight:  4.5 oz.

Housing Material:  AW10 in polycarbonate enclosure.

Mounting:  Screw tabs.

Degree of Protection:  Nema 4.

Model:  AW14 – AW10 switch in ABS enclosure.

Dimensions (WxHxD):  1-15/16 x 3-3/16 x 1-11/16 inches (50 x 85 x 43 mm).

Weight:  4.5 oz.

Housing Material:  AW10 in ABS enclosure.

Mounting:  Screw tabs.

Degree of Protection:  Nema 1.

Pneumatic switches. PS20A.

Low cost signaling alternative. Switch enclosure accepts an air hose connection. When the attached hose is compressed, air is forced into the diaphragm, activating a switch. The signal is sent to the motor controls.

Door Length:  Up to 18 ft in length.

Wireless (RF) version operates at a distance up to 100 ft depending on conditions.

Warranty:  1 year.

Model PS20A:  Pneumatic switch only. Wired.

Electrical Components:

Coil cords.

Retracting reels.

Junction boxes.

EXECUTION

EXAMINATION

Do not begin installation until the substrates have been properly constructed and prepared.

If substrate preparation is the responsibility of another installer, notify Architect in writing of unsatisfactory preparation before proceeding.

PREPARATION

Clean surfaces thoroughly prior to installation.

Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

INSTALLATION

Install in accordance with manufacturer's instructions approved submittals and in proper relationship with adjacent construction.

Be sure the installation is in compliance with UL 325.

FIELD QUALITY CONTROL

Field Inspection:  Coordinate field inspection in accordance with appropriate sections in Division 01.

** NOTE TO SPECIFIER ** Include if manufacturer provides field quality control with onsite personnel for instruction or supervision of product installation, application, erection, or construction. Delete if not required.

Manufacturer's Services:  Coordinate manufacturer's services in accordance with appropriate sections in Division 01.

CLEANING AND PROTECTION

Clean products in accordance with the manufacturers recommendations.

Touch-up, repair or replace damaged products before Substantial Completion.

END OF SECTION